LEW ELECTRIC TECHNICAL SPECIFICATIONS

SECTION 16143 - PVC FLOOR BOXES

Specifier Note:  To turn off Specifier Notes, click Tools/Options/View/Hidden Text.

- GENERAL

  - SUMMARY

    - This Section includes the following:

Specifier Note:  Retain applicable floor boxes and covers below.  Boxes are UL listed for concrete floors.

      - Round PVC Floor Boxes.

      - Cover plates and flanges.

      - Accessories.

    - Related Sections:

      - Section “Cast-in-Place Concrete” for casting boxes into concrete floors.

      - Section “Basic Electrical Materials and Methods” for installation of floor boxes.

      - Section “Raceways and Boxes” for conduit and tubing.

  - REFERENCES

    - ASTM B26/B26M-02 - Standard Specification for Aluminum-Alloy Sand Castings.

    - ASTM B 209-02a - Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate.

    - ASTM B 221-02 - Standard Specification for Aluminum and Aluminum-Alloy Extruded Bars, Rods, Wire, Profiles, and Tubes.

    - ASTM B 283-99a - Standard Specification for Copper and Copper-Alloy Die Forgings (Hot-Pressed).

    - ASTM D1784-99ae1 - Standard Specification for Rigid Poly(Vinyl Chloride) (PVC) Compounds and Chlorinated Poly(Vinyl Chloride) (CPVC) Compounds.

    - NFPA 70 – National Electrical Code; 2002.

    - UL 514C – Standard for Nonmetallic Outlet Boxes, Flush-Device Boxes and Covers; 1996.

  - SUBMITTALS

    - Product Data:  Manufacturer’s catalog data, product descriptions and installation instructions for each product specified.

    - Maintenance Instructions:  For floor boxes and covers for inclusion in maintenance manual.

    - Coordination Drawings:  Show locations, method of attachment and support for floor boxes.

  - QUALITY ASSURANCE

    - Source Limitations:  Obtain floor boxes and covers from one source and a single manufacturer.

    - Floor Boxes and Accessories:  Listed and labeled in accordance with NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

    - Comply with NFPA 70.

  - DELIVERY, STORAGE, AND HANDLING

    - Store products in manufacturer’s unopened packaging until ready for installation.

  - WARRANTY

    - Warrant against defects in material and workmanship for a 10 years after substantial completion.

- PRODUCTS

  - MANUFACTURERS

    - Acceptable Manufacturer:  LEW Electric Fittings Co.; 1801 W St Charles Rd, Maywood, IL 60153, Tel:  708-345-2075, Fax:  708-345-6490, email:  lewelectric@worldnet.att.net, www.lewelectric.com.

Specifier Note:  Delete one of the following two paragraphs.  Coordinate with Division 1 requirements.

    - Substitutions will not be allowed.

    - Substitutions will be accepted in accordance with Section 01600.

  - MATERIALS

    - Aluminum:  ASTM B 26/B 26M, Alloy A356.0-T6.

    - Brass:  ASTM B 283-99a.

    - PVC:  ASTM D 1784-99ae1.

  - FLOOR BOXES

    - PVC Floor Box:  UL 514C, 4 9/16 inch (114 mm) diameter, 90 cu. in. floor box, with (2)  3/4 inch (19 mm) and (2) 1 inch (25 mm) hubs, concrete cover cap, preformed partitioning slots and screw anchoring flanges.

  - COVER PLATES AND FLANGES

    - Single Service Covers:

      - Screw Plug Cover Plate:  Round brass cover plates, 1/8 inch (3 mm) thick, with threaded holes to accept screw plugs.

        - Style:  (2) 1 1/2 inch (38 mm) screw plugs for duplex receptacle.

        - Style:  Combination screw plug; 2 inch (50 mm) and 1/2 inch (13 mm) for com./data receptacles.

        - Style:  Combination screw plug; 2 inch (50 mm) and 3/4 inch (19 mm) for com./data receptacles.

        - Style:  Combination screw plug; 2 inch (50 mm) and 1 inch (25 mm) for com./data receptacles.

        - Style:  Single 2 inch (50 mm) screw plug.

        - Size:  4 inch (100 mm) diameter.

      - Metal Round Flip Lid Cover Plate:  Pin hinged, flanged cover plates 1/4 inch thick, fabricated for seamless attachment to floor box with screws of same material as cover plate.

        - Style:  Single hinged.

        - Style:  Dual hinged.

        - Size:  5 3/4 inch (144 mm) diameter.

        - Size:  5 1/4 inch (131 mm) diameter.

        - Material:  Brass.

        - Material:  Aluminum.

      - Plastic Round Flip Lid Cover Plate:  Pin hinged, 5 3/4 inch (144 mm) diameter flanged cover plates, fabricated for seamless attachment to floor box with screws.

        - Color:  Brown.

        - Color:  Ebony.

        - Color:  Gold.

        - Color:  Gray.

        - Color:  Tan.

        - Color:  White.

    - Multi-Service Covers:

      - Screw Plug Cover Plate:  5 3/4” (144 mm) diameter round cover plates, 1/8 inch (3 mm) thick, with threaded holes to accept screw plugs.

        - Style:  (2) 1 1/2 inch (38 mm)  screw plugs and (2) 1/2 inch (13 mm) plugs.

        - Style:  Combination screw plug; 2 inch (50 mm) and 1/2 inch (13 mm) and (2) 1/2 inch (13 mm) plugs.

        - Style:  Combination screw plug; 2 inch (50 mm) and 3/4 inch (19 mm) and (2) 1/2 inch (13 mm) plugs.

        - Style:  Combination screw plug; 2 inch (50 mm) and 1 inch (25 mm) and (2) 1/2 inch (13 mm) plugs.

      - Plastic Round Flip Lid Cover Plate:  Pin hinged, 5 3/4 inch (144 mm) diameter flanged cover plates with (2) 1/2 inch (13 mm) screw plugs, fabricated for seamless attachment to floor box with screws.

        - Color:  Brown.

        - Color:  Ebony.

        - Color:  Gold.

        - Color:  Gray.

        - Color:  Tan.

        - Color:  White.

  - ACCESSORIES

Specifier Note:  Retain applicable accessories below.

    - Floor Box Accessories:

      - Slide-in PVC partition.

      - Leveling ring adapter for round flanged cover plates.

      - PVC looping connector.

      - Universal adapter ring for metallic and non-metallic covers.

    - Cover Plate Accessories:

      - Mounting Plates:

        - Duplex Mounting Plate.

        - GFI/Decora Mounting Plate.

        - Single Receptacle/Data Mounting Plate.

  - FINISHES – COVERS, FLIP LIDS AND SCREW PLUGS

    - Brass:  Hand-Rubbed Finish:  M31-M34 (Mechanical Finish:  directionally textured, fine satin; Mechanical Finish:  directionally textured, hand rubbed).

    - Aluminum Plate and Sheet:  ASTM B 209, Alloy 6061-T6.

    - Aluminum Extrusions:  ASTM B 221, Alloy 6063-T6.

    - Aluminum Castings:  ASTM B 26/B 26M, Alloy 443.0-F.

- EXECUTION

  - EXAMINATION

    - Verify substrates are ready to receive floor boxes prior to installation.  Report any inconsistencies or discrepancies to the Architect.

    - Install floor boxes only after unsatisfactory conditions have been corrected.

  - INSTALLATION

    - Install supports to permanently and solidly attach floor boxes.

    - Install floor boxes flush with finish flooring.

    - Install temporary covers during construction to prevent the accumulation of foreign material in boxes.  Leave temporary covers in-place until installation of finished cover plates.

    - Install specified cover plates for each product in accordance with the manufacturer’s written instruction.

  - CLEANING AND PROTECTION

    - Repair or replace damaged products prior to substantial completion.

    - Clean exposed surfaces in accordance with manufacturer’s written instructions prior to substantial completion.

    - Protect installed products until project completion.